## Latest
Set point (ppm)
|  |  |  | Currently | Alternation
① | DeZn&MS Area | 17 sets | HH | 10 | 10 |  | HH detect
|  |  | H | 4 | 5
② | H2S Area | 10 sets | HH | 10 | 10 |  | HH detect
|  |  | H | 4 | 5
Count 3 detectors from 87 detectors
③ | Other Area | 17 sets | HH | 10 | 10 |  | HH detect over 3 sec |  | more than 3 detectors | H2S Shutdown(Box-in) & H2S Gas Injection for DeZn/MS Stop (106UZ800)
|  |  | H | 4 | 5
|  | （3 sets） | H0 | 0.1 | 0.1 |  | HH detect
④ | Boundary | 8 sets | HH | 0.2 | 0.2 |  | HH detect | over 3 sec |  | CB Alarm
|  |  | H | 0.1 | 0.1
| Boundary (Additional) | 35 sets | HH | 0.2 | 0.2 |  |  |  | Count 2 detectors from 43 detectors
|  |  | H | 0.1 | 0.1 |  | HH detect over 3 sec |  | more than 2 detectors
⑤ | H2S Building | 20 sets | HH | 10 | 10 |  | Both detect, Blower discharge and inside room |  |  | Change over gas flow lin from ATM to H2S SR03 (109/209SIF153ABCD)
|  |  | H | 4 | 5
Detail Tag Grop
| Group. | Area | Qty. | Tag | Location | Set point (ppm)
[6 empty] | Currently | Alternation
| ① | DeZn & MS Area | 17 | 105AT904 | 105TK01 | HH : 10.0 H : 4.0 | HH : 10.0 H : 5.0
|  |  |  | 105AT901 | 105TK03
|  |  |  | 105AT902 | 105TK05
105AT910
|  |  |  | 105AT912 | 106VE01
|  |  |  | 106AT909 | 106VE02
|  |  |  | 106AT908 | 106VE03
|  |  |  | 106AT907 | 106VE04
|  |  |  | 106AT906 | 106VE05
|  |  |  | 106AT905 | 106VE05
106AT915
106AT904
106AT903
106AT902
106AT901
106AT911
106AT906
| ② | H2S Area | 10 | 109AT115 | Sulfur Filter 2F | HH : 10.0 H : 4.0 | HH : 10.0 H : 5.0
|  |  |  | 109AT116 | Sulfur Filter GF
|  |  |  | 109AT212 | 109VE01 GF
|  |  |  | 109AT213 | 109BW03 GF
|  |  |  | 109AT214 | 109SR03 GF
|  |  |  | 109AT215 | 109VE05 GF
|  |  |  | 109AT216 | 109SR02 GF
|  |  |  | 109AT217 | 109HX22 GF
|  |  |  | 209AT212 | 209VE01 GF
|  |  |  | 209AT213 | 209BW03 GF
| ③ | Other Area | 17 | 101AT401 |  | HH : 10.0 H : 4.0 | HH : 10.0 H : 5.0
001AT003
|  |  |  | 001AT001 | HPAL(CB) entranse
001AT006
001AT005
001AT008
|  |  |  | 001AT007 | Workshop West
|  |  |  | 001AT009 | TJCP Office entranse
|  |  |  | 001AT104 | Product Warehouse
|  |  |  | 001AT105 | MS/H2S Substation
|  |  |  | 001AT101 | Water Treatment area
|  |  |  | 001AT301 | Limestone Substation
|  |  |  | 001AT302 | VSLC shelter entranse
|  |  |  | 111AT301 | Limestone South ditch
|  |  |  | 001AT201 |  | H0 : 0.1 | H0 : 0.1
001AT202
103AT903
| ④ | Boundary | 8 | 112AT901 | Water Intake | HH : 0.2 H : 0.1 | HH : 0.2 H : 0.1
|  |  |  | 111AT943 | Limestone Guard House
|  |  |  | 106AT931 | South of DeZn area
|  |  |  | 101AT909 | Main Gate Guard House
|  |  |  | 101AT907 | Bridge of Ore Prep
|  |  |  | 101AT901 | Culvert-12
|  |  |  | 101AT903 | Culvert-11
|  |  |  | 101AT905 | North of Coal Yard
|  | Boundary (Additional) | 35 | 101AT911 | 1 | HH : 0.2 H : 0.1 | HH : 0.2 H : 0.1
|  |  |  | 101AT913 | 2
|  |  |  | 101AT915 | 3
|  |  |  | 101AT917 | 4
|  |  |  | 101AT919 | 5
|  |  |  | 101AT921 | 6
|  |  |  | 101AT923 | 7
|  |  |  | 101AT925 | 8
|  |  |  | 101AT927 | 9
|  |  |  | 101AT929 | 10
|  |  |  | 101AT951 | 11
|  |  |  | 101AT953 | 12
|  |  |  | 101AT955 | 13
|  |  |  | 101AT957 | 14
|  |  |  | 101AT959 | 15
|  |  |  | 101AT961 | 16
|  |  |  | 101AT963 | 17
|  |  |  | 101AT965 | 18
|  |  |  | 101AT967 | 19
|  |  |  | 101AT969 | 20
|  |  |  | 101AT971 | 21
|  |  |  | 101AT973 | 22
|  |  |  | 101AT975 | 23
|  |  |  | 101AT977 | 24
|  |  |  | 101AT979 | 25
|  |  |  | 101AT981 | 26
|  |  |  | 106AT933 | 27
|  |  |  | 106AT935 | 28
|  |  |  | 106AT937 | 29
|  |  |  | 106AT939 | 30
|  |  |  | 106AT941 | 31
|  |  |  | 106AT943 | 32
|  |  |  | 112AT903 | 33
|  |  |  | 112AT905 | 34
|  |  |  | 112AT907 | 35
| ⑤ | H2S Building | 20 | 109AT601A | 109HX11AB | HH : 10.0 H : 4.0 | HH : 10.0 H : 5.0
|  |  |  | 109AT601B | 109BW02 Discharge
|  |  |  | 109AT602A | 109VE02
|  |  |  | 109AT602B | 109BW03 Discharge
|  |  |  | 109AT620A | 109QC01
|  |  |  | 109AT621 | 109QC01
|  |  |  | 109AT622 | 109VE01
|  |  |  | 109AT615 | 109BW04AB Discharge
|  |  |  | 109AT616 | 109BW04AB Discharge
|  |  |  | 109AT620B | 109BW01AB Discharge
|  |  |  | 209AT601A | 209HX11AB
|  |  |  | 209AT601B | 209BW02 Discharge
|  |  |  | 209AT602A | 209VE02
|  |  |  | 209AT602B | 209BW03 Discharge
|  |  |  | 209AT620A | 209QC01
|  |  |  | 209AT621 | 209QC01
|  |  |  | 209AT622 | 209VE01
|  |  |  | 209AT615 | 209BW04AB Discharge
|  |  |  | 209AT616 | 209BW04AB Discharge
|  |  |  | 209AT620B | 209BW01AB Discharge
Modification Result